| Title: | 2019/05 - Uncharted Electricity Cable Strike |
| --- | --- |
| What Happened / Impact? | Photo / Sketches |
| A groundworker was hand-digging a trial hole to locate a known ESB cable and other utilities in the footpath when the shovel he was using encountered an unmarked, uncharted, pot ended cable. The strike resulted in a minor flash and some smoke was also emitted. Luckily there was no injury to the operative undertaking the ground works. The operative had thought that that bit of concrete over the cable was just lying in the ground as there was no signal being emitted from the Cable Avoidance Tool (CAT) when it was used in the direction of the blue arrow, only from the red. It was during the action of attempting to prise this piece of concrete out that the pot-ended cable cover must have ruptured. The groundworkers had scanned the ground using the CAT and it had picked up the main cable; this was the only cable that was marked on the ESB drawing. No sand or marker tape was detected. Other controls utilised were (a) utility drawings, (b) a permit to dig, (c) an approved Risk Assessment Method Statement (RAMS) for the activity, (d) CSCS-trained LUGS operative, and (e) provision of a fully calibrated CAT. Example of pot ended cable | All the services in the footpath were laid in the direction of the blue arrow and the pot ended cable was running at a right angle to these. |
| Why it Happened? |
| The ESB personnel who came to repair the cable stated that it was probably an old service to a street light that was removed some time in the past. The cable was uncharted on the utility drawings and no indicator sand or tape was used. Pot ended cables are perhaps the most dangerous and difficult cable to locate and several accidents have occurred because excavators have damaged them. Locating using passive signals alone (using power frequency and radio frequency modes) can only find cables carrying current and/or reradiating radio signals. Generally, pot ended cables cannot be located with the universal CAT because pot ends do not carry current even though they are under voltage, so they do not radiate any power frequencies. To be detectable in Radio Frequency, the cable has to be sufficiently long to have a radio frequency current flowing through it, but because pot ends tend to be short length and are ungrounded there is no current path for the RF signal so with a conventional passive locating procedure they are “invisible”. |
| Immediate Learnings / Recommendations |
| Follow the requirements of ESB Networks and other Utilities providers and “Dial before you Dig”. Review all potential dig zones with the utility owner representative prior to digging in order to service locations on the utility drawings provided by the utility owner. Ensure that a robust Permit to Dig procedure and form are always used in conjunction with a location specific Risk Assessment and brief all involved personnel appropriately prior to commencement of works. Use only insulated tools when hand-digging in the vicinity of buried cables. Remember, if you suspect a cable is encased in concrete, please do not break around it, you must contact the utility owner in order to first get the cable switched off. |
| For Further Information: | Gas Networks Dial Before You Dig: Call 1850 42 77 47 or email: dig@gasnetworks.ie ESB Networks’ Central Network Mapping: Call 1850 928 960 / 01-8582060 or email: dig@esb.ie HSA’s Code of Practice for Avoiding Danger from Underground Services: Code_of_Practice_for_Avoiding_Danger_from_Underground_Services_.html ESB Networks’ Safe Construction and the Electricity Network: safe-construction-with-electricity-2018.pdf |